**UMG 605 Pro / UL / Ethernet + Profibus / 20-55V AC / 20-77V DC**

High-performance network analyser according to IEC 61000-4-30 class A / S

Suitable for measurement in all levels of TN & TT networks as well as in IT networks with voltage transformers for recording current, voltage, frequency, active, apparent & reactive power (per phase & total) in the frequency range 15 - 440 Hz, power factor & cos phi, active, apparent & reactive energy total as well as purchase and delivery of active & reactive energy (4-quadrant measurement) in separate memory values, 4 tariffs, continuous true RMS measurement.

Modbus RTU & TCP master function for network connection to own or higher-level software systems of max. 31 DIN rail or front panel devices as well as energy meters, data loggers & expansion modules per master device of the manufacturer's current product series. Ethernet gateway function as well as integration of Modbus RTU-certified third-party products after specific integration test via generic Modbus profiles. Simultaneous supply of the communication interfaces as well as parallel operation of 4 Modbus TCP ports.

Functional extensions via installable APPs as well as already pre-installed APPs with the following range of functions on the web server: Graphical display of online & historical measured values as well as comparison & interpretation of the recorded measured values with the power quality characteristics as well as their limit values according to IEC 61000-2-4 & EN 50160.

Freely programmable logical & mathematical functions for evaluating the measured data, the digital inputs and outputs & external ModBus variables via 7 graphic, exchangeable programmes (cycle >= 200 ms) such as limit value monitoring, weekly timer, etc.

Legally compliant, certified measurement procedure & measurement accuracy according to IEC 61000-4-30 class A / S

Complete provision of measured values for comparison of voltage quality characteristics as well as their limit values according to IEC 61000-2-4 in industrial supply networks and at the power transfer point (PCC) according to EN 50160.

Measurement of the positive, negative and zero sequence system as well as calculation of the resulting percentage voltage unbalance according to IEC 61000-4-30, rotating field direction as well as crest factor of voltage & current. Total harmonic distortion (THD-I & THD-U), total demand distortion (TDD), single harmonics (even / odd) & interharmonics for current & voltage up to the 63rd harmonic, K-factor as well as flicker measurement according to DIN EN 61000-4-15:2011 class F3.

Sampling rate of 20 kHz with 400 measuring points per period & output of the measured values via the interfaces (cycle >=200 ms), acquisition of transient events >50 µs, acquisition of over- & undervoltage for visualisation as well as short-term interruptions with 10 ms acquisition cycle, level acquisition of ripple control signals, half-wave rms recorder for events & event display (over- & undervoltage, voltage interruption, overcurrent) in waveform. 128 MB internal measured data memory (flash) freely configurable by the user, clock with buffering.

Accuracy classes according to IEC 61557-12 at 50/60 Hz:

Active energy: 0.5S - 1 / current: 0.25 / voltage: 0.1

Top-hat rail mounting, 107.5 x 90 x 82 (WxHxD), 6 TE wide, monochrome LCD - display, 2 keys, protection class IP 20, protection class: II, net weight: 350 g, heat dissipation: max. 3.2 W, UL 61010-1 certified.

Supply voltage:

Nominal range: 20 V - 50 V AC, 20 V - 70 V DC Frequency range (AC): 45 - 65 Hz

Overvoltage category: 150 V CATII

Voltage measurement:

3 Ph. + N (L-N / L-L) max.: 277 / 480 V

3 Ph. without N/PE (L-L) max.: 480 V

Overvoltage category: 300V CAT III

Current measurement:

Quantity: 4x

Measuring range / resolution: 5 mA to 6 A rms / 0.1 mA

Overvoltage category: 300V CAT III

Data interfaces:

Modbus (RS485), Ethernet (RJ45), Profibus (DSUB-9) Modbus (RS232)

Data protocols:

Modbus RTU & TCP, TCP/IP, DHCP, HTTP, NTP, SMTP Ethernet Gateway, FTP, TFTP, Profibus DP/V0, BACnet IP (optional).

Digital outputs:

Number / type: 2x optocoupler outputs

Function type: Pulse or limit value output

Supply: 24 V DC passive, galvanically insulated

Switching current / voltage / frequency: 50 mA effective / 60 V DC / 20 Hz

Digital inputs:

Number: 2x

Type of function: Digital or pulse input

Switching voltage level: 0 - 28 V DC

Counting frequency: max. 20 Hz

Temperature measurement:

Quantity / type / total burden: 1x 3-wire measurement with 4 kOhm

Compatible sensors: PT100/1000, KTY83/84

Delivery includes:

Mounting accessories, documentation, parameterisation & evaluation software in basic version, adjustment of the design to the practical application as well as the measured variables incl. their recording intervals, compatible current transformer set min. Kl. 0.5 all-phase, measuring transformer disconnect terminals with screw connection 0.2 - 10 mm², bridges as well as DIN rail clamp for DIN rail mounting according to DIN VDE 0100 - 557.5.3.1, configuration and parameterisation of the unit (e.g. mains form, transformer ratios, addressing of the communication interfaces), delivery, installation as well as connection.

Primary current at measuring point: '.........'. A.

Unit version with data communication protocol

BACnet / IP (Yes / No): '.........'.

Manufacturer: Janitza electronics GmbH

Type: UMG 605 Pro

Art.no.: 5216229